## Slide 1
Andrew Streifel
Hospital Environment Specialist
University of Minnesota Medical Center
Ventilation for Energy Management and Infection Prevention
Hosted by Dr. Lynne Sehulster
Centers for Disease Control, Atlanta
www.webbertraining.com
September 17, 2015

## Slide 2
Andrew Streifel
Hospital Environment Specialist
University of Minnesota Medical Center
• 38 years service at U of Minnesota infection prevention.
• Visited over 400 hospitals & assisted in IAQ infection issues.
• Technical expert for ASHRAE, CDC, FGI & other organizations.
• Goal to provide evidence based training for prevention of
infections during construction & maintenance practice.
• Provide guidance for infectious disease prevention design concepts.

## Slide 3: Why is energy important to infectious disease management?
Mermazadeh and Xu 2012 recommend site specific risk analysis because increasing or decreasing the room air exchange rate by as little as one air change per hour can result in a differene of $150-250 per year in heating and cooling costs for that room.
Dr. Mermazadeh is the Director of Technical Services NIH.

## Slide 4: Electrical Usage at Typical Hospital

## Slide 5: Gas Consumption in a Typical Hospital

## Slide 6: Levels of Risk
Healthy person
Chronic obstructive pulmonary disease
Diabetes
Steroids
Cancer - solid tumor
HIV infection-end stage of spectrum
Organ transplant
  Kidney/heart
  Lung/liver
Malignancy - leukemia/lymphoma
Bone marrow transplant (BMT) allograft

## Slide 7: What Drives High Energy Use in Healthcare Facilities
•Ventilation
  -High Efficiency Filters
    +90 to 99.97% efficiency
•Indoor Air Quality Standards
-12 to 20 room air exchanges per hour
-waste anesthetic gas, heat, electro-cautery smoke
-microbial shedding and surgical aerosols (no standards)
•Airborne Infection, Protective Rooms, ICU’s and Surgery
-high air exchanges for heat and aerosol control some recirculate
-exhaust from airborne isolation rooms
•IAQ control for temperature, humidity, minimum outdoor air
•Domestic water temperatures
•Laboratory equipment
•Therapeutic and Diagnostic equipment
• 24/7/365 100% ready days with emergency backup

## Slide 8: Incidence of Healthcare Associated Infections (HAI), U.S. 2011-2012
  Annual morbidity: 721,800 – Decrease from 1.7 million estimated in 2002 (NEJM, 2014)
  1 in every 25 inpatients has at least 1 HAI
  Most common: Pneumonia and surgical site infection
  Most frequent organism: Clostridium difficile
Annual mortality: 100,000 estimated in 2002 (Klevens, Public Health Reports, 2002)
Direct costs associated with HAI: $28.4-$45 Billion (Scott, CDC Paper, 2012)
Incidence associated with construction unknown; multiple outbreak papers published

## Slide 9: Factors Involved in the Spread of Infectious Diseases
Droplet nuclei transmission dynamics
Nature of dust levels
Health & condition of individual’s nasopharyngeal mucosal lining
Population density in a particular location
Ventilation of the location

## Slide 10: Standard Precautions Against Disease Transmission
Early identification of microbes
Development of appropriate SOPs
Use of PPE including:
  Masks & gloves
  Disinfection strategies
  Vaccination
  Appropriate ventilation design

## Slide 11: Indoor Air Quality

## Slide 12
 | Fungi | Bacteria | Viruses
Numerous reports in HCF | Aspergillus spp. Mucorales | M. Tuberculosis | Measles virus Varicella-zoster virus
Atypical, occasional reports | Acremonium spp. Fusarium spp Pseudoallescheria boydii Scedosprorium spp. Sporothrix cyanescens | Acinetobacter spp. Bacillus spp. Brucella spp. Staphylococcus aureus Group A. Streptococcus | Smallpox virus Influenza viruses Respiratory syncytial virus Adenoviruses Norwalk-like virus
Airborne in nature; airborne transmission in HCF not described | Coccidioides immitis Cryptococcus spp. Histoplasma capsulatum | Coxiella burnetti (Q fever) | Hantaviruses Lassa virus Marburg virus Ebola virus Crimean-Congo Virus
CDC Guideline for Environmental Infection Control Guidelines 2003
Organisms Associated with Airborne Transmission

## Slide 15: Recent examples of the frequency of invasive aspergillosis
Underlying condition | Incidence | Reference/year
Acute myeloid leukaemia | 8% | Cornet, 2002
Acute lymphatic leukaemia | 6.3% | Cornet, 2002
Allogeneic HSCT | 11-15% | Grow, 2002; Marr, 2002
Lung transplantation | 6.2-12.8% | Minari, 2002; Singh,2003
Heart-lung transplantation | 11% | Duchini, 2002
Small bowel tranplantation | 11% | Duchini, 2002
AIDS | 2.9% | Libanore, 2002

## Slide 16
How far can Airborne Bacteria & Viruses Travel?
Coughing 1-5 feet 160+ feet
Sneezing 8-15 feet 160+ feet
Singing, Talking 1-3 feet 160+ feet
Mouth Breathing 1-3 feet 160+ feet
*Diarrhea 5 feet+ 160+ feet
*As a Result of Toilet Water Aerosolization and Mechanical Fan Dispersion into outdoor air (2003 Hong Kong SARS Virus Epidemic)
Large/Small Droplets Droplet Nuclei

## Slide 17
1. Mucus/water encased by the infector or by toilet water. These quickly fall to the ground after traveling up to 1-3 feet.
Stages of Infectious Droplets & Droplet Nuclei
2. Mucus/water coating starts to evaporate. These will travel 3-5 feet before falling to the ground. These droplets can become droplet nuclei.
3. Mucus/water coating has totally evaporated coating the viron particles. These are Droplet Nuclei which are so microscopic they can float in the air.

## Slide 18
Diameter of Droplet (µm) | Evaporation time (sec) | Distance fallen in ft. (before evaporation)
200 | 5.2 | 21.7
100 | 1.3 | 1.4
50 | 0.31 | 0.085
25 | 0.08 | 0.0053
Evaporation Time & Falling Distance of Droplets Based on Size
Adapted from: Wells, W.F., 1955, Airborne contagion and air Hygiene, Harvard University Press, Cambridge, Mass.
*particles discharged at 6 ft. > 140µm tend to fall to the ground
*particles discharged at 6 ft. < 140µm evaporate to droplet nuclei

## Slide 19: Infectious Droplets & Droplet Nuclei travel lengths

## Slide 20: Airborne Transmission depends on people to launch viruses into the air. People can shed this many Flu Viruses into the air as tissue culture infecting doses (TID)
1. Coughing 3,000+ TID
2. Sneezing 3,000+ TID
3. Breathing: Nose-None
4. Talking/Singing 1,000+ TID
5. Vomiting 1,000+ TID
6. *Diarrhea 20,000+ TID
* As a result of Toilet Water Aerosolization

## Slide 21
Droplet Nuclei Travel Within Buildings
In hospitals re-circulated air is filtered > 90%

## Slide 22: ● Viruses Evaporate faster in Low Humidity levels thus creating More Droplet Nuclei. ● Low humidity allows droplet nuclei to stay airborne longer as the droplets do not absorb water weight which would cause them to fall to the ground. ● Indoor Air currents both created by HVAC systems and people movement assure that droplet nuclei will remain airborne Indefinitely. ● This allows HVAC systems to remove and redistribute droplet nuclei throughout the building to infect more occupants.
Low Indoor Humidity Increases Droplet Nuclei Levels (winter)

## Slide 23: 1) Indoor humidity levels (winter) in the Northern Hemisphere especially in North America and Europe are between 15-35%. 2) Studies have proven that there is no “flu season” in the tropics where indoor humidity levels stay above 40% all year long.
There is a DIRECT correlation between low indoor humidity in winter and increases in influenza morbidity and mortality

## Slide 24
ASHRAE Standard 55-1992 recommends: Relative Humidity between 20% and 60%
Less than 50% RH for dust mite control
Facility Guidelines Institute
Design Parameters of Selected Areas
Function of Space Relative Humidity % Design Temperature °F/°C
Classes B & C Operating Rooms 20-60 68-75/20-24
Burn unit 40-60 70-75/21-24
Newborn intensive care 20-60 70-75/21-24
Patient room(s) max 60 70-75/21-24
Protective environment room max 60 70-75/21-24
Airborne Isolation anteroom N/R N/R
ASHRAE STD 170 HEALTHCARE VENTILATION 20% RH CHANGE

## Slide 25
There are six basic types of natural ventilation systems:
• single-side corridor
• central corridor
• courtyard
• wind tower
• atrium and chimney
• hybrid (mixed-mode) ventilation.
World Health Organization Pub/Natural Ventilation for Infection Control in Healthcare-2009

## Slide 29
★ The performance in either thermal comfort or infection control is
unsatisfactory. In terms of infection control, it means the magnitude of
the ventilation rate.
★★ The performance is fair.
★★★ The performance is acceptable, but compromise may be needed in terms
of thermal comfort.
★★★★ The performance is good in terms of both thermal comfort and airborne
infection control.
★★★★★ The performance is very good (satisfactory) in terms of both thermal
comfort and infection control.
Applicability of natural ventilation systems
Natural ventilation for infection control
in health-care settings.

## Slide 30
monitor
corridor
Negative Pressure Room for Airborne Infection Isolation
Bathroom
Monitorr
Corridor
Bathroom
Positive Pressure Room for Protective Environment
30
Notes: Environmental Validation Infection Control
Andrew Streifel
30
25

## Slide 31
AIA & ASHRAE DESIGN GUIDELINES FOR VENTILATION
CDC EIC MMWR JUNE 6, 2003

## Slide 32
Notes: 32

## Slide 33
Notes: 33

## Slide 34
Notes: 34

## Slide 36
Benefits of Active Beams in Healthcare
Reduction in air handling equipment
Minimization and elimination of ductwork
Reduction in reheat
Quiet operation
Improved indoor air quality
Reduced risk of cross contamination
Planning for New Ambulatory Care Center University of Minnesotan Medical Center 2014

## Slide 38
Chill beam advantage is to
separate the cooling component
with the air supply to save energy.

## Slide 39
•Must have access for cleaning
•Must not condense on the surfaces of the chill beam
•A sealed curtain wall helps keep humidity out of the building

## Slide 41
What is displacement ventilation?
Piston airflow
Displacement like piston airflow
moves air in single direction
that displaces air as it moves
The intent being not to mix the
air but pushes is it.

## Slide 42
Short circuiting airflow
Mixing ventilation
Normal Room Ventilation Conditions

## Slide 43
The advantages of Displacement ventilation
Energy saving and moving air out of the breathing zone

## Slide 44
Waiting rooms and atriums are
very good applications for using
this kind of air delivery. DV is also
common in auditoriums
Unique diffusor design allows them to be
Incorporated into building structure at lower
Elevations in respective rooms.

## Slide 46
Advantage of Displacement Ventilation for Infection Prevention and
Energy Management
Infection Prevention
-Room temps may seem warmer
due to delivery temp higher.
-Rising temp creates upward
buoyance to lift particles
-When infectious particle above
breathing zone safe?
Energy Management
-Air delivered to room for
comfort already >60F
-Lower energy costs
-Decrease air exchange
for room by using 6 ft
instead of 8 ft for calculation
Disadvantage: Difficult to find space in a patient room to deliver air low

## Slide 47
Heat Wheels can Reclaim Energy
Aware of air flow direction (clean to dirty) and need to clean the wheel
How is it maintained?

## Slide 48: Causes of Ventilation Deficiencies
Plugged Filters
Plugged Temperature Control Coils
Duct Leakage
Dust on Fan Blades
Fan Belt Slippage
Uncalibrated Control Equipment
  Digital Controls
  Pneumatic Controls
    Plugged sensors

## Slide 49
HVAC – Chilled Water System

## Slide 52: Deep Cleaning Process Recover Coil Heat Transfer Performance
Result: More air and cooler air

## Slide 54
Impact of Air Flow On Room Particle Contamination

## Slide 56: Filter Engineering Solutions Impact of Innovative Filter Technologies
glass fibers
synthetic fibers
Face Loading
Depth Loading
MAINTAIN
Synthetic electro static fibers may degrade quickly

## Slide 58: Removal Efficiency In-Situ by Particle Size and Resistance to Flow
Direction of Airflow
Particle Counter
Before
After
Before filter
12176 p/ft^3
After filter
40 p/ft^3
>99% reduction

## Slide 61: Room 206
SUPPLY
Door

## Slide 63
Patient Mock-up Room Leakage Application Overview
Why should we seal rooms anyway??

## Slide 67
Notes: 29

## Slide 68: Case Study- Barrier Management “Leakage”
Total Barrier Management
Infection control
Sound
Energy/ Movement
UL systems
Total Barrier Management practices increase build integrity beyond UL systems with additional secondary attributes
DISCLOSURE HILTI SPONSORED STUDY

## Slide 69
Staff/Housekeeping/Clean equipment in-flow
Patient in-flow
Patient/Staff/Housekeeping/Dirty Equipment out-flow
HLIU FLOW
Dirty
Decon
Dirty
Decon
Dirty
Ante
Dirty
Ante
Clean
Ante
Clean
Ante
Dirty
Ante
Dirty
Ante

## Slide 70
PROPOSED AIR PRESSURE
-5pa
-5pa
-7.5pa
-7.5pa
-7.5pa
-7.5pa
-10pa
-10pa
-2.5pa
-2.5pa
-2.5pa
-2.5pa
-5pa
-5pa
Interlocking doors

## Slide 71
Staff/Housekeeping/Clean equipment in-flow
Patient in-flow
Patient/Staff/Housekeeping/Dirty Equipment out-flow
*Loss of corridor space and 2 x Nurse Alcoves

## Slide 75
Application Test Series – Complete Overview
Source: Testing implemented by The Energy Conservatory. Testing completed w/ Duct Blaster fan and micromanometer measuring flows from 10 to 1500 CFM.
Blower Test # | Test Application | Status | CFM Per Application
1 | ToW | Open | 7000
2 | ToW | Sealed | 98.85
3 | BoW | Open | 98.85
3 | BoW | Sealed | 40.63
4 | Plumbing | Open | 816.3
5 | Plumbing | Sealed | 41.3
6 | Low Voltage | Open | 191.8
7 | Low Voltage | Sealed | 45.96
8 | Electrical Boxes | Open | 135.6
9 | Electrical Boxes | Sealed | 46.52
10 | Mechanical * | Open | 135.6
11 | Mechanical | Sealed | 46.59

## Slide 76: Case Study- Barrier Management
Total Barrier Management
Infection control
Sound
Energy/ Movement
UL systems
Total Barrier Management practices increase build integrity with life Safety and fire secondary attributes
The most common requirement for control is the UL or life safety considerations as they
pertain to fire and smoke control. Hospital
corridors and other potential fire hazard
need to be sealed
Fire management in healthcare has provided safety to millions of healthcare building occupants resulting in enormous strides in
fire management through regulation. NFPA,
Life safety 99 and 101.
What additional benefits can be realized?
LIFE SAFETY/FIRE

## Slide 77: Case Study- Barrier Management
Total Barrier Management
Infection control
Sound
Energy/ Movement
UL systems
Total Barrier Management practices increase build integrity and sound migration secondary attributes
Additional benefits of a sealed room include sound mitigation. It is common acoustical knowledge that sound transmission can be partially mitigated by impeding air movement. This practice occurs where airport noise is managed with sealed houses to minimize
sound wave infiltration. HIPPA requires
privacy from hearing patient conditions.
Explain some of the physics of sound transmission
SOUND MITIGATION

## Slide 78: Case Study- Barrier Management
Total Barrier Management
Infection control
Sound
Energy/ Movement
UL systems
Total Barrier Management practices increase build integrity and energy & comfort secondary attributes
Building design in healthcare includes inoperable windows to prevent infiltration of uncontrolled air. Comfort factors are essential to convalescence therefor to maintain
temperature between 68 and 72 can
be difficult without controlled ventilation.
Leakage reduction will require less heating and cooling??
Does a sealed room/building provide ventilation energy efficiency?
Provide some energy statistics??
ENERGY/COMFORT

## Slide 79: Case Study- Barrier Management
Total Barrier Management
Infection control
Sound
Energy/ Movement
UL systems
Total Barrier Management practices increase build integrity and infection prevention secondary attributes
Control of aerosol important principal for airborne infectious agents causing tuberculosis or aspergillosis depends on airflow control. Aerosol management due to patient derived symptoms needs masking and special room ventilation. Aerosol control is dependent on airflow direction intensity.
Excess room leakage will diminish pressure management design. A sealed room will help provide consistent direction for prevention of occupational exposures to droplet nuclei containing Mycobacterium tuberculosis or chicken pox
INFECTION PREVENTION

## Slide 80: Infection Prevention and Ventilation
Air volumes must be maintained to assure cleaning the air of contaminants
Impediments include: plugged equipment that needs cleaning or change out of filters
Aspiring to have good air quality requires routine maintenance to assure AC/hr, filtration and pressure.

## Slide 82
September 24 (Free Teleclass) EVIDENCE VS. TRADITION: EXAMINING THE EVIDENCE OF BATHING TO REDUCE HAI’S Kathleen Vollman, Advanced Nursing LLC Sponsored by Sage Products (www.sageproducts.com) September 28 (Free British Teleclass ... Broadcast live from the 2015 IPS conference) WHAT DID THE ROMANS EVER DO FOR US? Carole Fry, Healthcare Infection Society September 29 (Free British Teleclass ... Broadcast live from the 2015 IPS conference) FAECAL TRANSPLANT TO TREAT CLOSTRIDIUM DIFFICILE DISEASE Dr. Jonathan Sutton, Betsi Cadwaladr University Health Board, Wales September 30 (Free British Teleclass ... Broadcast live from the 2015 IPS conference) THE EMERGENCE OF MERS: FROM ANIMAL TO HUMAN TO HUMAN Professor Ziad Memish, Prince Mohammed Bin Abdulaziz Hospital, Saudi Arabia October 14 (FREE WHO Teleclass - Europe) THE USE OF SOCIAL MEDIA IN SUPPORT OF GLOBAL INFECTION PREVENTION AND CONTROL