## Slide 1: Infection Control Risk Assessment Issues ... New Construction
Andrew Streifel
Hospital Environment Specialist
strei001@umn.edu
Hosted by Dr. Lynne Sehulster
www.webbertraining.com
October 24, 2019

## Slide 2: Levels of Risk
Healthy person
Chronic obstructive pulmonary disease
Diabetes
Steroids
Cancer - solid tumor
HIV infection-end stage of spectrum
Organ transplant
  Kidney/heart
  Lung/liver
Malignancy - leukemia/lymphoma
• Bone marrow transplant (BMT) allograft
Greatest Risk

## Slide 3: New Construction
Hand cleansing
Ventilation pressure management
Bathrooms # of sinks
Water quality temperature/stagnation/conserve
Utility rooms
Construction quality best practice
ICU/OR/NNICU/special vent rooms
Energy and water conserve
Surge capacity
Water damage response
Tie-ins and utility outages

## Slide 4: What and Where Risk During Construction AIR & WATER
Patients
  Immune suppressed
  Convalescent areas
Departments
  Surgery
  Radiation
  Catheterization
  Equipment cleaning
Procedures
  Bedside or areas
Issues for Environmental Infection Control
  Utility planning emergent and routine outages
  Ventilation management during projects
  Water quality assurance (opportunistic pathogens)

## Slide 5: Design Guidelines
Design criteria
  Facilities Guidelines Institute
  Centers for Disease Control & Prevention
  Uniform Building Code
  International Building Code
  National Fire Protection Association
  Plumbing code
  Electrical code
  Mechanical code
  Pharmacy code USP 797
  other

## Slide 6: Best Practice Manual from APIC
•Policies
•Construction Documents
•Dust Control
•Water Sampling
•Air Monitoring
•Education and Training
•Equipment Resources
•Architectural and Design
•Floor Recovery and Mold Abatement
•Trends and Issues
•Construction Resources
•Glossary
2015

## Slide 8
In addition:
ICRA based on FGI
-timing
-team
-design
-surfaces/finishes
-construction
-compliance
-mitigation response
-monitoring
-communication
CODE requirements
Interim Life Safety
-coordination
-fire watch inspection
-IP elements

## Slide 9: Master Specifications for UMMC

## Slide 10
New Construction
ICRA in APIC Infection
Prevention Manual for
Construction and
Renovation 2015
Overview for Planning
Large Projects

## Slide 11
Index
I. The Infection Control Risk Assessment
II. Internal collaboration and consideration
III. Recommendations and Regulatory Resources to be incorporated: External
IV. Recommendations and Regulatory Resources to be incorporated: Internal
V. Operational Issues
VI. Areas Requiring Infection Control Sign off for Design and Specifications
VII. Communication: Technical Review User Group
VIII. Construction
IX. Brief Summary Following-Completion of the South Building & Riverside
X. The UMMC/UMACH Infection Control ICRA Planning and Design Elements for
Consideration and Discussion:
a. Construction
b. Renovation
c. Commissioning
d. Appendix A: Construction/Renovation APIC Matrix
e. Appendix B: Containment and Monitoring
Construction Worker Hospital Training
First Day First Hour
TABLE OF CONTENTS

## Slide 15
FGI & ASHRAE DESIGN GUIDELINES FOR VENTILATION
CDC EIC MMWR JUNE 6, 2003

## Slide 19: Key Components
Exterior of building
  Keeps out water and air infiltration
Ventilation Systems
  Provides comfort and infection safety of air
  Need evaluation tools
Water Systems
  Becoming important for sustainability
  Protect for drinking, sanitation and clinical application
  Out of control water in healthcare

## Slide 20
Notes: 20

## Slide 21
Notes: 21

## Slide 23
NATURAL VENTILATION

## Slide 24
★ The performance in either thermal comfort or infection control is
unsatisfactory. In terms of infection control, it means the magnitude of
the ventilation rate.
★★ The performance is fair.
★★★ The performance is acceptable, but compromise may be needed in terms
of thermal comfort.
★★★★ The performance is good in terms of both thermal comfort and airborne
infection control.
★★★★★ The performance is very good (satisfactory) in terms of both thermal
comfort and infection control.
Applicability of natural ventilation systems
Natural ventilation for infection control
in health-care settings.
WHO Natural Ventilation 2009

## Slide 25
Notes: 25

## Slide 26
Benefits of Active Beams in Healthcare
Reduction in air handling equipment
Minimization and elimination of ductwork
Reduction in reheat
Quiet operation
Improved indoor air quality
Reduced risk of cross contamination
Planning for New Ambulatory Care Center University of Minnesotan Medical Center 2014

## Slide 28
Chill beam advantage is to
separate the cooling component
with the air supply to save energy.

## Slide 30
* Baseline Preliminary Review & Program Analysis
*Pre-design
*Schematic Design
*Design Development
*Construction Documents
*Construction Implementation
*Facilities Commissioning
*Occupancy
*Certification for Use
•What infection control
principals need to be developed?
-ventilation
-plumbing
-airborne infection isolation
-surgery
-immune suppression
-disaster planning
•Identify locations for need.
-user group collaboration
•Construction methods
-water damage management
-construction methods
-validation process
Phases of Construction

## Slide 31: AIA 2010 Guidelines for Design And Construction of Hospitals & Health Care Facilities
Latest in an over 60-year series of guidelines specific for design and construction of hospital and other health care facilities
    Nursing Facilities; Outpatient Facilities
    Rehabilitation Facilities; Psychiatric Hospital
    Mobile, Transportable, and Relocatable Units
    Hospice Care; Assisted Living
    Adult Day Care Facilities
    Glossary Tables
    ASHRAE Std 170 Ventilation for HCF inclusion

## Slide 32: Built Environment Projects
Renovation
  Program changes
  Maintenance & utility upgrade
  Preconstruction
    Discovery/Utilities, shutoffs, etc.
    Recycle equipment
New Construction
  Planning Design and Construction
What infection control training is needed for contractor supervisors and workers?

## Slide 34
PRECAUTIONS DURING CONSTRUCTION
INDOOR PROJECTS (RENOVATION) OUTDOOR PROJECTS (NEW)
Employee training Employee training
Barrier management Dust control
Water damage Noise and vibration
Demolition precautions Pest control
Dust migration and control Building material storage
Debris and material transport Water damage management
Access routes to work area Sanitation and break areas
Outages (electrical and plumbing) Tie in building issues
Portable filter usage Commissioning-air & water
Noise and vibration Shell spaced-build out
Sanitation and break areas
Commissioning -air & water
Communication Communication
Emergency response Emergency response
Water damage reporting Water damage reporting
Changing work phases Material crane location
ICRA precautions during occupancy Changing ICRA precautions pre occupancy
Water Quality Water Quality
Stagnant water flushing Stagnant water flushing
Testing water requirements Testing water requirements
Punch list Punch list
Critical sinks drinking water Critical sinks drinking water

## Slide 35
Awareness Factors by Trade |  |  |  |  |  |  |  | 
 | Plumber | HVAC | Electrician | Painter | Laborer | IT Specialist | Riggers | Specialty Trade
Awareness Factors |  |  |  |  |  |  |  | 
Water damage | x |  | x | x | x | x |  | x
Mold discovery | x |  | x | x | x | x |  | x
Outages | x | x | x |  |  |  |  | x
ICRA | x | x | x | x | x | x | x | x
Water event response | x |  |  |  | x |  |  | 
Stagnant water | x |  |  |  |  |  |  | 
Building material storage/stocking | x | x | x | x | x | x | x | x
Noise/vibration | x | x | x |  | x | x | x | x
Track dirt | x | x | x | x | x | x | x | x
Wall/slab penetrations | x | x | x |  | x | x |  | 
Material transport | x | x |  |  | x |  | x | x
Biocide application |  |  |  | x | x |  |  | x
Room/wall seal application |  |  |  | x | x |  |  | 

## Slide 36
monitor
corridor
Negative Pressure Room for Airborne Infection Isolation
Bathroom
Monitorr
Corridor
Bathroom
Positive Pressure Room for Protective Environment
Intended Usages:
Procedure/Treatment Rooms
Bronchoscopy
Autopsy
Emergency Rooms
Intended Usages:
Immune Compromised Patient Rooms
Operating Rooms
36
Notes: Environmental Validation Infection Control
Andrew Streifel
36
25

## Slide 37
The solution to pollution is dilution…………
Higher room air exchanges purify if filters are working.

## Slide 38: Operating Room Ventilation
Comfort control
  Temperature and humidity
    Cooling capacity for heat gain essential
  Anesthetic gas management
    Problematic due to no permissible exposure limit
    Scavenging and high room air exchange needed
  Infectious disease control
    Smoke plume management
    Airborne microbes? Contact microbes?

## Slide 39
The airflow pattern in OR’s
must overcome thermal
buoyance and maintain a down
ward flow of air

## Slide 40
Vertical airflow 30 to 40 lfpm at surgery site

## Slide 41: Age of Air Concept for particle movement

## Slide 42
Air movement velocity (fps) and decay of carbon dioxide can
demonstrate ventilation efficacy.

## Slide 45: Surgical Smoke Generated During Hip Resection
Chart: 

## Slide 46: Controlling Airborne Infectious Agents in Surgery
Extra pulmonary disease (TB, BBP)
  Scavenging of smoke or aerosol?
  Personal protective equipment
Human shed microbes
  Air velocity over surgical site
  Overcome thermal plume with 35-40 lfpm velocity
Air handling deficiencies
  Booster steam or humidification problems (condensation)
  Insufficient air flow (gas accumulation)
  Depressurized operating rooms (air balance)

## Slide 47: Functional Performance Testing Baseline Data for Future Reference
List:
- patient care unit
- room number
- type of room
- monitoring system
- local display monitor
- AC/hr
- differential pressure
- offset
- airflow direction
- room size square feet
- supply volume
- return/exhaust volume

## Slide 48: Case Study- Barrier Management “Leakage”
Total Barrier Management
Infection control
Sound
Energy/ Movement
UL systems
Total Barrier Management practices increase build integrity beyond UL systems with additional secondary attributes
DISCLOSURE HILTI SPONSORED STUDY

## Slide 49: Case Study- Barrier Management
Total Barrier Management
Infection control
Sound
Energy/ Movement
UL systems
Total Barrier Management practices increase build integrity and infection prevention secondary attributes
Control of aerosol important principal for airborne infectious agents causing tuberculosis or aspergillosis depends on airflow control. Aerosol management due to patient derived symptoms needs masking and special room ventilation. Aerosol control is dependent on airflow direction intensity.
Excess room leakage will diminish pressure management design. A sealed room will help provide consistent direction for prevention of occupational exposures to droplet nuclei containing Mycobacterium tuberculosis or chicken pox
INFECTION PREVENTION

## Slide 50
Staff/Housekeeping/Clean equipment in-flow
Patient in-flow
Patient/Staff/Housekeeping/Dirty Equipment out-flow
HLIU FLOW
Dirty
Decon
Dirty
Decon
Dirty
Ante
Dirty
Ante
Clean
Ante
Clean
Ante
Dirty
Ante
Dirty
Ante

## Slide 51
PROPOSED AIR PRESSURE
-5pa
-5pa
-7.5pa
-7.5pa
-7.5pa
-7.5pa
-10pa
-10pa
-2.5pa
-2.5pa
-2.5pa
-2.5pa
-5pa
-5pa
Interlocking doors

## Slide 52: Competency Principals for Hospital Design to Control Certain Infectious Diseases
Ventilation indoor air quality control
  Pressure intensity
  Air exchanges for dilution
  Filtration for cleanliness
  Clean to dirty airflow
Surface management
  Durable and Cleanable
Water Quality assurance
  Flush or Disinfect

## Slide 57: Air sample interpretation (problem)
Indoor/Outdoor ratio >1 (Precipitation not present)
Indoor problem area different from indoor control
Indoor organisms are not similar to outdoor organisms
Aggressive samples have higher counts than passive samples.

## Slide 58: Surface sampling strategy
Indoor problem
Indoor control
Plate control
Looking for:
Suspected poor maintenance
Area with previous water damage
METHODS
Rodac contact plate (viable)
Swab plate (viable)
Tease tape (non-viable)
Vacuum method (viable)

## Slide 60
AIA & ASHRAE DESIGN GUIDELINES FOR VENTILATION
CDC EIC MMWR JUNE 6, 2003
VENTILATION ASSURANCE BEFORE PATIENT OCCUPANCY

## Slide 61: Objectives for Infection Control during Construction in Healthcare Facilities
Respectful of patients
Control aerosols
Maintain a clean environment
Prevent water damage
Respond to emergencies
Provide documentation
Be trained & communicate